## Project Dashboard
COPELAND DESIGN STUDIO — PROJECT DASHBOARD
Copeland Group Services ¦ Engineering Design Toolkit ¦ v1.6 — Smart Workbook
Current Version |  | v1.6
Version Name |  | Smart Workbook
Status |  | ACTIVE
Current Sprint |  | Sprint 2 — Smart Engine
Sprint Start |  | 2026-06-27
Sprint End |  | 2026-07-11
Toolkit Owner |  | Copeland Group Services
Maintained By |  | PaulMc
SPRINT 2 — SMART WORKBOOK FEATURES
Task | Status | Owner | Version
Camera Schedule — smart entry sheet | COMPLETE | PaulMc | v1.6
Camera type dropdown (13 types) | COMPLETE | PaulMc | v1.6
Auto camera numbering (CAM-001…) | COMPLETE | PaulMc | v1.6
Resolution dropdown + auto bitrate suggest | COMPLETE | PaulMc | v1.6
Lens dropdown + H-FoV auto-calculation | COMPLETE | PaulMc | v1.6
Daily storage auto-calculation (GB/day) | COMPLETE | PaulMc | v1.6
Storage Calculator sheet | COMPLETE | PaulMc | v1.6
PoE Budget sheet (per switch) | COMPLETE | PaulMc | v1.6
Bill of Materials (auto-aggregated) | COMPLETE | PaulMc | v1.6
Design validation summary | COMPLETE | PaulMc | v1.6
Vector symbol library (SVG/CAD) | PLANNED | PaulMc | v1.7
Professional drawing sheet upgrade | PLANNED | PaulMc | v1.7
Survey forms — CCTV (Word+PDF) | PLANNED | PaulMc | v1.2
Survey forms — Intruder (Word+PDF) | PLANNED | PaulMc | v1.2
Full Design Manual v2.0 | PLANNED | PaulMc | v2.0

## Camera Schedule
COPELAND GROUP SERVICES — CCTV CAMERA SCHEDULE
Project: [Project Name] ¦ Drawing Ref: CAM-001 ¦ Rev: P1 ¦ Date: 2026-06-27 ¦ Prepared by: PaulMc
SCHEDULE SUMMARY — AUTO-CALCULATED
Total Cameras |  | Camera Count | PoE Cameras |  | Power | Total Storage / Day (GB) |  | GB/day | Storage — 14 days (GB) |  | Retention | Storage — 31 days (GB) |  | Retention | Total PoE Draw (W) |  | Power Budget
CAM No. | Location / Area | Camera Type | Make / Model | Resolution | Lens | H-FoV ° | Ht (m) AFF | Mount | IR (m) | IP Rating | Compression | Bitrate Mbps | GB / Day | Retention days | Power | PoE Class | Watts | Switch / Port | NVR / Ch
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
31
COLOUR KEY: |  |  |  | Yellow = Dropdown — click cell for list |  |  | Green = Formula — auto-calculated |  |  | White/Grey = Free text entry

## Storage Calculator
COPELAND GROUP SERVICES — STORAGE CALCULATOR
Based on camera schedule data ¦ Adjust bitrates on Camera Schedule sheet
STORAGE BY RETENTION PERIOD — PULLED FROM CAMERA SCHEDULE
Retention Period | Days | Total GB | Total TB | HDD Qty (4TB drives) | HDD Qty (8TB drives) | NVR Min (TB) | Notes
14 days (CCTV CoP minimum) | 14
28 days (Standard commercial) | 28
31 days (Recommended) | 31 | [5 empty] | Add 20% headroom for OS/metadata
60 days (High risk / financial) | 60
90 days (Archive requirement) | 90
BITRATE REFERENCE TABLE
Resolution | Scene | H.265 Mbps | H.264 Mbps | GB/day H.265 | GB/day H.264 | Notes
2MP (1080p) | Internal / low movement | 1.5 | 3 | 16.2 | 32.4
2MP (1080p) | External / busy | 3 | 6 | 32.4 | 64.8
4MP (2.7K) | Internal / low movement | 3 | 6 | 32.4 | 64.8
4MP (2.7K) | External / busy | 5 | 10 | 54 | 108
8MP (4K) | Internal / low movement | 6 | 12 | 64.8 | 129.6
8MP (4K) | External / busy | 10 | 20 | 108 | 216
12MP | Any | 12 | 24 | 129.6 | 259.2 | High bandwidth — plan network carefully
NVR SIZING NOTES
1. Always add 20% headroom to calculated storage for OS, metadata, and smart features.
2. Cameras using smart compression (H.265+) can reduce storage by 50–70% vs H.264.
3. Motion-triggered recording reduces storage significantly — confirm with client requirements.
4. RAID configurations reduce usable capacity: RAID 5 = (N-1)/N × raw. Factor into drive count.
5. Cloud backup adds cost but protects against local NVR failure — recommend for high-risk sites.
6. Retention of 31 days recommended as standard. Martyn's Law events: 30 days post-event minimum.

## PoE Budget
COPELAND GROUP SERVICES — PoE POWER BUDGET
IEEE 802.3af / at / bt ¦ Always add 20% headroom ¦ Verify switch spec before ordering
PoE SWITCH SCHEDULE — ENTER SWITCH DETAILS BELOW
Switch ID | Location | Make / Model | Total PoE Budget (W) | Standard | Ports | Notes
SW-001
SW-002
SW-003
SW-004
SW-005
SW-006
SW-007
SW-008
PoE DEVICE SUMMARY — PULLED FROM CAMERA SCHEDULE
Camera Count (PoE) | Total PoE Draw (W) | Recommended Min Budget (W) | Largest Switch Budget Entered (W) | Status
PoE STANDARDS REFERENCE
Standard | Max Power at PSE | Typical Use | Voltage | Max Current | Pairs Used
IEEE 802.3af (PoE) | 15.4 W | 2MP cameras, basic audio, intercoms | 44–57 V | 350 mA | 2 pair
IEEE 802.3at (PoE+) | 30 W | 4MP cameras, PTZ, IR, wireless AP | 50–57 V | 600 mA | 2 pair
IEEE 802.3bt Class 6 (PoE++) | 60 W | High-power PTZ, pan+tilt+heater | 50–57 V | 960 mA | 4 pair
IEEE 802.3bt Class 8 (PoE++) | 90 W | PTZ + heater + wiper | 50–57 V | 1440 mA | 4 pair
DESIGN RULES
1. Switch PoE budget must be ≥ sum of all connected device maximum draw + 20% headroom.
2. Do not rely on per-port power alone — check the total switch PoE budget (pool), not just port spec.
3. Long cable runs (>80m) cause voltage drop — use PoE extenders or mid-span injectors for distant cameras.
4. Outdoor cameras with IR heaters may draw up to 90W in winter — use Class 8 rated switches.
5. ANPR cameras with illuminators: verify total draw including illuminator on same PoE port.
6. Always document switch make/model and firmware version in the as-built record.

## Bill of Materials
COPELAND GROUP SERVICES — BILL OF MATERIALS
Camera counts auto-calculated from Camera Schedule ¦ Prices and supplier entered manually
CAMERA TYPE COUNT — AUTO FROM CAMERA SCHEDULE
Camera Type | Count | Make / Model | Unit Price (£) | Total (£) | Supplier | Part No. | Notes
Fixed Dome
Vandal Dome
Mini Dome
Bullet
Turret
PTZ
ANPR / LPR
Thermal
Multi-Sensor
Body-Worn
Covert / Pinhole
Fisheye 360°
Box
TOTAL CAMERAS
ADDITIONAL EQUIPMENT
Item Description | Qty | Make / Model | Unit Price (£) | Total (£) | Supplier | Part No. | Notes
Network Video Recorder (NVR)
PoE Network Switch
Patch Panel
19" Rack / Cabinet
UPS — Uninterruptible Power Supply
Fibre Media Converter (pair)
HDMI / IP Monitor
PTZ Keyboard Controller
Cable — Cat6 UTP (m)
Cable — Fibre OS2 (m)
Cable Trunking / Conduit (m)
Junction Boxes
Fixings & Sundries (allow)
PROJECT GRAND TOTAL (EX VAT)

## Design Validation
COPELAND GROUP SERVICES — DESIGN VALIDATION
Pre-issue checklist ¦ Complete before issuing any drawing for review or construction
CCTV DESIGN — PRE-ISSUE CHECKS (DS-001 / BS EN 62676-4)
Ref | Check | Pass/Fail/N/A | Notes
Coverage | All critical areas identified in survey have camera coverage
Resolution | Camera resolution appropriate for identification vs overview requirement
IR | IR capability confirmed where lighting is inadequate (lux level checked)
Storage | Retention period confirmed with client — calculation on Storage Calculator sheet
Network | Network infrastructure capacity confirmed — switch PoE budget on PoE Budget sheet
GDPR | CCTV signage specified — data retention does not exceed identified need
Cybersecurity | Network segregation noted — default password policy referenced in spec
Numbering | All cameras numbered sequentially CAM-001… on drawing and schedule
Schedule | Camera schedule complete — all fields populated, no blanks in mandatory columns
Drawing | Drawing number follows CGS format — title block complete
Revision | Revision number set to P1 (preliminary) or A (for review) as appropriate
Notes | General notes block on drawing — BS EN 62676-4 referenced
Legend | Legend on drawing — all symbols used are listed
INTRUDER ALARM — PRE-ISSUE CHECKS (PD 6662 / BS EN 50131)
Ref | Check | Pass/Fail/N/A | Notes
Grade | Grade 2 or Grade 3 confirmed against risk assessment
Detection | All entry points and vulnerable areas have detection
Signalling | Dual-path signalling specified for Grade 3
ARC | ARC category and response confirmed
Bell box | External sounder positions drawn and IP/IK rated
Panel | Control panel location confirmed — accessible, not in detection zone
Power | Standby power calculation — 12h standby minimum (Grade 2)
Zones | Detection zones numbered and named — logic in spec
ACCESS CONTROL — PRE-ISSUE CHECKS (BS EN 60839-11)
Ref | Check | Pass/Fail/N/A | Notes
Doors | All controlled doors on drawing — strike type specified
Fire | Fire alarm integration confirmed — fail-safe on alarm activation
DDA | Accessible entry point(s) identified — door force <30N
Anti-passback | Anti-passback required? — confirmed with client
Credentials | Credential type confirmed — card / mobile / biometric
Intruder link | Access control to intruder integration specified
GENERAL — ALL DISCIPLINES
Ref | Check | Pass/Fail/N/A | Notes
Standards | Relevant BS/EN standards referenced in drawing notes
Spec | Equipment specification issued alongside drawings
Contractor brief | Installation contractor briefed on any special requirements
As-built reminder | As-built drawing requirement noted in contract documents
Client sign-off | Client has signed off on coverage/spec before For Construction issue

## Release Notes
COPELAND DESIGN STUDIO — RELEASE NOTES
Version history and feature release record
Version | Date | Release Name | What's Included | Status | Owner
v1.0 | 2026-06-26 | Foundation | Project structure, 9 master documents (DS, SL, DT, SF, CS, EW, ES, CP, DM), design standards, symbol index, camera schedule reference, EcoWatch, event/Martyn's Law, client project index, design manual | RELEASED | PaulMc
v1.5 | 2026-06-26 | Foundation + Drawing Pack | Excel master workbook (5 sheets), A3 HTML engineering drawing sheet, CGS document numbering, client project 01–08 folder template | RELEASED | PaulMc
v1.6 | 2026-06-27 | Smart Workbook | Camera Schedule with 13 camera type dropdowns, auto-numbering (CAM-001…), lens H-FoV formula, bitrate suggestion, daily storage formula, PoE watts auto-calc. Storage Calculator with retention table. PoE Budget with switch schedule and budget check. Bill of Materials with auto camera counts and project grand total. Design Validation pre-issue checklist. | RELEASED | PaulMc
v1.7 | TBD | Professional Drawing Sheet | Upgraded A3 engineering drawing sheet, Copeland brand palette, premium typography, print-ready A3/A2 layouts | PLANNED | PaulMc
v1.2 | TBD | Survey Pack | 7 survey forms as Word + PDF: CCTV, Intruder, Access Control, EcoWatch, Event Security, Martyn's Law, Security Risk Assessment | PLANNED | PaulMc
v1.1 | TBD | Symbol Library | Full graphical symbol library: CAD blocks (.dwg), SVG set, PDF sheet — CCTV, intruder, access, EcoWatch, event | PLANNED | PaulMc
v2.0 | TBD | Copeland Design Studio | Full integrated platform — one workbook drives drawings, schedules, BOM, reports. Complete drawing template set A0–A4. Full Design Manual. | PLANNED | PaulMc